GridVision OpenDSS Studio — LECO BZ0109
Technical Manual & Electrical Calculation Specification

Comprehensive Technical Equations, Input File Data Mapping, Engineering Assumptions, and QSTS Power Flow Methodology

1. Executive Summary & Overview

This document provides the complete engineering specification for the GridVision OpenDSS Studio web application. The software performs Quasi-Static Time Series (QSTS) 3-phase 4-wire power flow simulations on the LECO Transformer BZ0109 low-voltage (400V/230V) distribution network. It integrates monthly billing consumption datasets, 15-minute smart meter Load Profiling (LP) interval records, rooftop solar PV inverter reports, and GIS geographic network topology.

2. Raw Data Ingestion & Input File Lineage

The software extracts customer demand, solar capacity, network topology, and smart meter measurements from specific input files, sheets, and columns as detailed below:

| Data Category | File Name & Path | Sheet Name & Column Headers | Extracted Parameters & Rules |
| --- | --- | --- | --- |
| GIS & Topology | network_map.json | Root JSON object: - poles[] - lines[] | Poles: id, lat, lon, is_tf (AR48T), feeder (F1–F8). Lines: from, to, length_m, conductor (ABC_70, Fly_AAC). |
| Billing & Demands | DATA_BZ0109.xlsx / account_pole_map.json | Sheet: DATA / Consumption Columns: ACCOUNT, POLE ID, CATEGORY / TARIFF, kWh columns | Account matching rule: strip leading zeros (e.g., '00024/1234' -> '24/1234'). Extracts monthly energy E_month and tariff class (R1, GP11, STL, I12). |
| Smart Meter LP | pole_voltage_compare.json / voltages_timeline.json | Sheet: LP Data Columns: CUSTOMER_REF, DATE, TIME, AVG._IMPORT_KW, AVG._EXPORT_KW, PHASE_A_VOLTAGE, PHASE_B_VOLTAGE, PHASE_C_VOLTAGE | 15-minute interval transformer net power P_meas(t) and pole measured phase voltages (Va, Vb, Vc). Used for calibration and measured vs. simulated comparison. |
| Rooftop Solar PV | BZ0109_solar_customers.csv / Solar Data V2 | Sheet: Solar Data V2 Columns: ACCOUNT / CUSTOMER, POLE ID, INVERTER_KW / CAPACITY | Extracts solar PV inverter capacity P_inv (kW) mapped to customer account and pole ID (11 accounts, 179.3 kW total capacity). |

3. Scientific & Engineering Assumptions

| Engineering Parameter | Scientific Assumption & Justification |
| --- | --- |
| Nominal System Voltage | Nominal Phase-to-Neutral voltage V_nom = 230.0 V (Phase-to-Phase V_LL = 400.0 V) at 50 Hz system frequency. |
| Statutory Voltage Limits | Statutory allowable voltage limits strictly enforced at 216.2 V (-6.0%) minimum under-voltage threshold and 243.8 V (+6.0%) maximum over-voltage threshold. |
| Transformer Rating | Distribution Transformer Tx_BZ0109 rated at 250 kVA, 11kV/0.4kV, Delta-Wye grounded configuration (%R = 1.0%, %X = 4.5%). |
| Customer Power Factor | Standard customer loads assigned a lagging power factor cos φ = 0.95 (tan φ = 0.329). Solar PV inverters operate at unity power factor (PF = 1.0). |
| Radial Tree Topology | The distribution network is modeled as a strict radial tree graph originating from transformer pole AR48T across 8 main distributor branches (F1 through F8). |
| Quasi-Static Time Series | QSTS evaluates 96 steady-state snapshot power flow solves per day (15-minute time steps) assuming fast transient dynamics settle within each interval. |
| Behind-the-Meter Netting | Smart meters record NET power flow (Import - Export). Internal home customer load behind the solar meter consumes a portion of solar output before reaching the meter. |
| Conductor Impedances | Aerial Bundled Conductors (ABC_70: R1 = 0.443 Ω/km, X1 = 0.09 Ω/km) and All Aluminum Conductors (Fly_AAC: R1 = 0.270 Ω/km, X1 = 0.30 Ω/km). |

4. Technical & Mathematical Equations

4.1. Customer Demand Allocation

P_avg,c = E_month,c / (N_days × 24)

Where E_month,c is the monthly billed kWh for account c from DATA_BZ0109.xlsx, N_days is the billing cycle days (e.g., 30 days). Converts energy into mean active power (kW).

4.2. Tariff-Shaped Customer Active & Reactive Load

P_c(t) = P_avg,c × s_tariff(c)(t) × α(t)
Q_c(t) = P_c(t) × tan(acos(PF))

Where s_tariff(c)(t) is the normalized 15-minute daily tariff profile vector for tariff class c (R1, GP11, STL, I12), α(t) is the hourly calibration multiplier, and PF = 0.95.

4.3. 15-Minute Solar Irradiance Curve & PV Output

c_irr(t) = max(0.0, 1.0 - ((h(t) - 12.25) / 5.5)^2)  for 6.0 <= h(t) <= 18.0
P_solar,k(t) = P_inv,k × c_irr(t) × β

Where h(t) = t/4.0 is hour of day (0.0 to 23.75), P_inv,k is installed inverter kW rating at pole k, c_irr(t) is normalized irradiance (0.0 at night, 1.0 at 12:15 solar noon), and β is irradiance scale.

4.4. Locked Export-Target Solar Calibration

P_pv*(t) = max(P_load(t) - P_meas(t), 0.0)

Where P_meas(t) is the measured transformer net power from LP data. Used in locked calibration mode so simulated net power tracks physical meter export when solar output exceeds load.

4.5. Global Active Power Conservation

P_TF,net(t) = P_load(t) - P_pv(t) + P_loss(t)

Where P_TF,net > 0 represents net power import from the 11kV grid through the 250kVA transformer, and P_TF,net < 0 represents net solar power export back to the 11kV grid.

4.6. OpenDSS 3-Phase 4-Wire Branch Voltage Drop

[V_a, V_b, V_c, V_n]_(k+1) = [V_a, V_b, V_c, V_n]_k - Z_4x4 × [I_a, I_b, I_c, I_n]_k

Where Z_4x4 is the 4-wire line impedance matrix derived from conductor resistance R and self/mutual reactance X for ABC/Fly overhead line codes.

4.7. Phase Voltage Averages & Unbalance Percentage

V_avg = (V_a + V_b + V_c) / 3.0
Unbalance % = ((max(V_a,V_b,V_c) - min(V_a,V_b,V_c)) / V_avg) × 100%

Calculates mean phase-to-neutral voltage V_avg and phase voltage unbalance percentage at any pole node across 3-phase conductors (lines 3485-3488 in index.html).

4.8. Transformer Loading Percentage

Loading % = (|P_TF,net(t)| / S_rated) × 100%

Where S_rated = 250 kVA. Measures transformer capacity utilization under import peak (evening) and export peak (solar noon).

4.9. Statistical Model Accuracy Metrics (RMSE & Pearson Correlation)

RMSE_kW = sqrt((1/N) × Σ (P_sim(t) - P_meas(t))^2)
RMSE_V = sqrt((1/M) × Σ (V_sim(k) - V_meas(k))^2)
ρ = Σ (P_meas - P_bar_meas)(P_sim - P_bar_sim) / [ sqrt(Σ (P_meas - P_bar_meas)^2) × sqrt(Σ (P_sim - P_bar_sim)^2) ]

Quantifies simulation accuracy against physical LP smart meter measurements for active power (kW), voltage (V), and daily shape correlation (ρ).

5. Execution & Simulation Workflow

1. Data Reading: FastAPI backend reads GIS coordinates, billing customer accounts, LP 15-minute readings, and solar inverter reports.
2. Topology Generation: BFS algorithm constructs the radial feeder graph from transformer pole AR48T and calculates cumulative electrical distance d(k) along line paths.
3. OpenDSS Script Generator: dss_generator.py writes master.dss, lines.dss, loads.dss, and pvsystem.dss files.
4. QSTS Solve Loop: opendss_runner.py steps sequentially through 96 15-minute intervals, solving nodal voltages, current flows, transformer loading, and line losses.
5. Result Visualization: The web browser displays 24-hour time-series charts, Leaflet voltage heat maps, measured vs. simulated phase cards, and distance vs. voltage feeder profiles.